## JBS (2A)
Estimate Quantity (Only figures) | Item Detailed Specification Description | Work Type eg., Earth Work, Electrical works..etc., (Upto 200 Characters) | Item short Description | APSS/Morth CI.Number (Upto 200 characters) | Rate INR upto 2 Decimals | UOM (upto 50 Characters) | Amount INR (Upto 2 Decimals)
1 | Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | Erection work | Erection of 11kv AB Switch incl earthing | As per relevent standard specification | 3200 | EA | 3200
4 | S&Fix-3x300sqmm 11KV UG Cb OD End Kit | Laying | S&Fix-3x300sqmm 11KV UG Cb OD End Kit | As per relevent standard specification | 3236 | EA | 12944
90 | Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench , 11 KV-1.05Mtrs.Along the CC / BT multi layer road. Lay-DR 11KV 3x300sqmm UG Cb CC/BT. | Laying | Lay-DR 11KV 3x300sqmm UG Cb HG/BC/CC/BT | As per relevent standard specification | 631.06 | M | 56795.4
10 | Raising of double run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) Raise-DR 11KV 3x300sqmm UG Cb on support | Excavation work | Raise-DR 11KV 3x300sqmm UG Cb on support | As per relevent standard specification | 275.4 | M | 2754
1 | Supply of CI Pipe earthing 80mm dia 2.75m long | Supply | S-CI Pipe earthing 80mm dia 2.75m long | As per relevent standard specification | 2789 | EA | 2789
1 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.6M dia x 0.5 M height . | Erection work | ERECT. OF LINES-Providing of earthing | As per relevent standard specification | 1234.2 | EA | 1234.2
15 | Supply of 6" B Class GI pipe 5mm thck 20Kg/M | Supply | S-6" B Class GI pipe 5mm thck 20Kg/M | As per relevent standard specification | 1044 | M | 15660
1 | ERECTION OF LINES : Providing of RCC collar to existing earth pit.Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M he | Erection work | ERECT. OF LINES-Providing of RCC collar | As per relevent standard specification | 386 | EA | 386
1 | Fabricate-11VK Seating Channel | Fabrication Work | Fabricate-11VK Seating Channel | As per relevent standard specification | 131 | EA | 131
1 | Supply of Betonite powder for earthing | Erection work | Supply of Betonite powder for earthing | As per relevent standard specification | 650 | BAG | 650
20 | Supply of MS Bolts & Nuts,Washers etc., | Erection work | Supply of MS Bolts & Nuts,Washers etc., | As per relevent standard specification | 91.25 | KG | 1825
12 | Fab Back clamps with 75 x 8 mm MS Flat | Fabrication Work | Fab Back clamps with 75 x 8 mm MS Flat | As per relevent standard specification | 31 | EA | 372
6 | Supply of Pad clamps 100X100X15 mm 1 panth 600A | Supply | Supply of Pad clamps 100X100X15 mm 1 panth 600A | As per relevent standard specification | 264 | EA | 1584
3 | Sup Spacer T- clamps -Twin zebra/Panther | Supply | Sup Spacer T- clamps -Twin zebra/Panther | As per relevent standard specification | 508 | EA | 1524
6 | Erection of 11 M long PSCC pole | Erection work | Erection of 11 M long PSCC pole | As per relevent standard specification | 4336.85 | EA | 26021.1
2 | Erection of 9/10/11Meter Box pole | Erection work | Erection of 9/10/11Meter Box pole | As per relevent standard specification | 2643.83 | EA | 5287.66
1 | Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | Erection work | Erection of 11kv ABSwitch incl earthing | As per relevent standard specification | 3200 | EA | 3200
5 | Supply & Fixing of 3x300sqmm 11KV UG Cb OD End Kit | Supply | S&Fix-3x300sqmm 11KV UG Cb OD End Kit | As per relevent standard specification | 3236 | EA | 16180
5 | Supply & Fixing of 3x300sqmm 11KV UG Cb StrgtThrJoint | Supply | S&Fix-3x300sqmm 11KV UG Cb StrgtThrJoint | As per relevent standard specification | 5947 | EA | 29735
12 | S-Suspension Clamp Assembly & Eye Hook-M | Supply | S-Suspension Clamp Assembly & Eye Hook-M | As per relevent standard specification | 65 | EA | 780
12 | Erect-Suspension Clamp Assbl &Eye Hook | Erection work | Erect-Suspension Clamp Assbl &Eye Hook | As per relevent standard specification | 8 | EA | 96
4 | S-Dead End Clamp Assembly & Eye Hook-M | Supply | S-Dead End Clamp Assembly & Eye Hook-M | As per relevent standard specification | 80 | EA | 320
4 | Erect-Dead End Clamp Assbl & Eye Hook | Erection work | Erect-Dead End Clamp Assbl & Eye Hook | As per relevent standard specification | 8 | EA | 32
2 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 0.76X0.76X1.83M | Excavation work | Exca Hard pit w/o blast 0.76X0.76X1.83M | As per relevent standard specification | 928 | EA | 1856
15 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 0.76X0.76X1.52M | Excavation work | Ex of Hard pit w/o blast 0.76X0.76X1.52M | As per relevent standard specification | 793 | EA | 11895
1 | Supply of CI Pipe earthing 80mm dia 2.75m long | Supply | S-CI Pipe earthing 80mm dia 2.75m long | As per relevent standard specification | 2789 | EA | 2789
1 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.6M dia x 0.5 M height . | Erection work | ERECT. OF LINES-Providing of earthing | As per relevent standard specification | 1234.2 | EA | 1234.2
480 | Excavation & laying of UG Cable in Single Run Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs along the CC / BT multi layer road requiring compressor. Laying of SR 11KV 3x300 Sq.mm UG cb CC/BT compsr | Laying | Lay-SR 11KV 3x300sqmm UG Cb CC/BT Compsr | As per relevent standard specification | 1073.94 | M | 515491.2 | *
20 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)Raise SR 11KV 3x300sqmm UG Cb on support | Excavation work | Raise-SR 11KV 3x300sqmm UG Cb on support | As per relevent standard specification | 144.08 | M | 2881.6 | *
20 | Supply of 6" B Class GI pipe 5mm thck 20Kg/M | Supply | S-6" B Class GI pipe 5mm thck 20Kg/M | As per relevent standard specification | 1044 | M | 20880
10.16 | Mass concreting of supports incl. cement, including cost of the elements | Mass concreting work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 66842.64
5 | Supply of Pre-cast cable Joint markers | Supply | Supply of Pre-cast cable Joint markers | As per relevent standard specification | 484 | EA | 2420
200 | Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench , 11 KV-1.05Mtrs.Along the CC / BT multi layer road requiring compressor. Lay-DR 11KV 3x300sqmm UG Cb CC/BT Compsr | Laying | Lay-DR 11KV 3x300sqmm UG Cb CC/BT Compsr | As per relevent standard specification | 1264.64 | M | 252928
400 | S-9" B Class GI pipe 7.3mm thck 28.8Kg/M | Supply | S-9" B Class GI pipe 7.3mm thck 28.8Kg/M | As per relevent standard specification | 1113 | M | 445200
9 | ERECTION OF LINES : Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location ex | Erection work | ERECTION OF LINES-Erection of 9.1M Pole | As per relevent standard specification | 2400 | EA | 21600
0.6 | Stringing of AB cbl 11 KV 3x185+70 Sqmm | Stringing | Stringing of AB cbl 11 KV 3x185+70 Sqmm | As per relevent standard specification | 41876.1 | KM | 25125.66
1 | Erect of HT Metering Box incl box cost | Erection work | Erect of HT Metering Box incl box cost | As per relevent standard specification | 5000 | EA | 5000
1 | Construction of Plinth for mounting HT Trivector meter of size 0.6mx0.3mx 0.9m (0.6m above GL with Brick Masonary (>&<)> 0.3m below GL with PCC 1:2:4 ) , with 1:2:4 CC bed 3" on top <(>&<)> with 1:4:8 CC bed 4" on bottom including cost of cement. | Construction work | Con of Plinth HTTVR meter 0.6x0.3x0.9m | As per relevent standard specification | 5202 | EA | 5202
4 | Erection of 9/10/11Meter Box pole | Erection work | Erection of 9/10/11Meter Box pole | As per relevent standard specification | 2643.83 | EA | 10575.32
4 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 0.76X0.76X1.83M | Excavation work | Exca Hard pit w/o blast 0.76X0.76X1.83M | As per relevent standard specification | 928 | EA | 3712
4.12 | Mass concreting of supports incl. cement, including cost of the elements | Mass concreting work | Mass concreting of supports incl. cement | As per relevent standard specification | 6579 | M3 | 27105.48
4 | Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | Paint work | Painting of RS Joist(1C RO, 2C Al.Paint) | As per relevent standard specification | 1132 | EA | 4528
2 | Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | Erection work | Erection of 11kv ABSwitch incl earthing | As per relevent standard specification | 3200 | EA | 6400
1 | Erect-HT Trivector Meter | Erection work | Erect-HT Trivector Meter | As per relevent standard specification | 1000 | EA | 1000
300 | Lay-4C/10C 2.5Sqmm Control Cable | Laying | Lay-4C/10C 2.5Sqmm Control Cable | As per relevent standard specification | 27 | M | 8100
1 | ERECTION OF EQUIPMENT Substations Erection of 11 KV LAS line type including earthing | Erection work | Erect of 11kvLA line type incl earthing | As per relevent standard specification | 505 | SET | 505
1 | Fix-GPRS Modem & Sim Card | Fixing | Fix-GPRS Modem & Sim Card | As per relevent standard specification | 300 | EA | 300
40 | Excavation & laying of UG Cable in Single Run Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths andfilling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabadprotective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs.Across the CC/ BT road crossing multi layer road requiring compressor wih hume pipe (cxcluding the cost ofHume Pipe) In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil / CC/BT Road. Lay-SR 11KV 3x300 Sqmm UG Cb HG/BC/CC/BT | Laying | Lay-SR 11KV 3x300sqmm UG Cb HG/BC/CC/BT | As per relevent standard specification | 465.46 | M | 18618.4 | *
10 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) Raise-SR 11KV 3x300sqmm UG Cb on support | Excavation work | Raise-SR 11KV 3x300sqmm UG Cb on support | As per relevent standard specification | 144.08 | M | 1440.8 | *
4 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | Fabrication Work | Fabrication of 175x85/150x75mm RS joist | As per relevent standard specification | 512.55 | EA | 2050.2
50 | Supply of GI Bolts & Nuts,Washers etc., | Supply | S-GI Bolts & Nuts,Washers etc., | As per relevent standard specification | 117.5 | KG | 5875
4 | Supply of CI Pipe earthing 100mm dia 2.75m long | Supply | S-CI Pipe earthing 100mm dia 2.75m long | As per relevent standard specification | 3486 | EA | 13944
4 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.6M dia x 0.5 M height . | Erection work | ERECT. OF LINES-Providing of earthing | As per relevent standard specification | 1234.2 | EA | 4936.8
4 | ERECTION OF LINES : Providing of RCC collar to existing earth pit.Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M he | Erection work | ERECT. OF LINES-Providing of RCC collar | As per relevent standard specification | 386 | EA | 1544
2 | Supply & Spreading of 20mm HBG metal | Supply | Supply & Spreading of 20mm HBG metal | As per relevent standard specification | 2113 | M3 | 4226
0.256 | Coping & Muffing-Iron Pole, Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | Erection Work | Coping & Muffing-Iron Pole | As per relevent standard specification | 3893.01 | M3 | 996.6106
2 | Supply of Danger boards with clamps | Supply | Supply of Danger boards with clamps | As per relevent standard specification | 116 | EA | 232
10 | Supply & Fixing of 3x300sqmm 11KV UG Cb OD End Kit | Supply | S&Fix-3x300sqmm 11KV UG Cb OD End Kit | As per relevent standard specification | 3236 | EA | 32360
12 | Provd-Dble Jumper 11KV SC Line | Supply | Provd-Dble Jumper 11KV SC Line | As per relevent standard specification | 265 | SET | 3180
15 | SupPad clamps 100X100X15 mm 1 panth 600A | Supply | SupPad clamps 100X100X15 mm 1 panth 600A | As per relevent standard specification | 264 | EA | 3960
1 | Supply & Erection of 11KV Indoor Metering Cubical | Supply | S&Erect-11KV Indoor Metering Cubical | As per relevent standard specification | 403389 | EA | 403389