## Sheet1
Schedule for the work "Power evacuation facilitates from EHT Bowrampet SS of 33kV HMT Hills from Pragathi nagar khaman to Pragathi Nagar Lake (HMT Hills road) with 33KV 3Cx400Sqmm Aluminium 2 run cable by tapping to newly proposed 100 sqmm AAA SCOH conductor at Pragathi nagar Khaman in Medchal Operation circle in Masterplan Sub-division-1 of WCGH division of RR circle under T&D Improvement works"
1. Memo.No.CGM/MP/Gr.Hyd/F./D.No.1296/23-24, Dt: 12.10.2023.
2. WBS No. S-1652-13-04-01-01-001
Sl.No | Estimate Quantity(Only Figures) | PARTICULARS | Work Type | Item Short Description | SWR No/APSS/Morth cl.No | Rate (INR) (Upto 2 Decimals) | UOM | Amount
1 | 700 | Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil/CC 33KV 3x400sqmm UG Cable | Elecy | Labour | SWR11972 | 749 | M | 524300
2 | 235 | Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. Across the CC/ BT road crossing multi layer road requiring compressor (excluding the cost of Hume pipe) 33KV 3x400sqmm UG Cable | Elecy | Labour | SWR11988 | 1587.07 | M | 372961.45
3 | 3700 | Laying of 2nd Cable in Excavated Trench | Elecy | Labour | SWR10988 | 204.1 | M | 755170
4 | 40 | Raising of double run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) | Elecy | Labour | SWR12004 | 323.85 | M | 12954
5 | 26 | Making of Straight through joint 33kv 3x400 xlpe | Elecy | Labour | SWR10382 | 5700.78 | EA | 148220.28
6 | 8 | Making of Outdoor/Indoor End Termination 33kv 3x400 xlpe cable | Elecy | Labour | SWR10387 | 2764.76 | EA | 22118.08
7 | 2 | Loading of 33KV 800 Amps AB Switch | Elecy | Labour | SWR10239 | 126 | EA | 252
8 | 2 | Un loading of 33KV 800 Amps AB Switch | Elecy | Labour | SWR10557 | 79 | EA | 158
9 | 2 | Erection of 33 KV AB Switch including alignment and earthing | Elecy | Labour | SWR10392 | 4500 | EA | 9000
10 | 12 | LOADING of R.S. Joists 175 x 85 mm | Elecy | Labour | SWR10204 | 76 | EA | 912
11 | 12 | UNLOADING of R.S. Joists 175 x 85 mm | Elecy | Labour | SWR10522 | 50 | EA | 600
12 | 0.9 | Loading of M.S.Channels, Angles, Flats & Rods etc., | Elecy | Labour | SWR10206 | 221 | TO | 198.9
13 | 0.9 | Un loading of M.S.Channels, Angles, Flats & Rods etc., | Elecy | Labour | SWR10524 | 185 | TO | 166.5
14 | 0.9 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 KM and upto 20 KM | Elecy | Labour | SWR10132 | 412.08 | TO | 370.872
15 | 4 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M | Elecy | Labour | SWR11040 | 990.68 | EA | 3962.72
16 | 4 | Excavation of pits in all soils except hard rock requiring blasting 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M (1.31 cum) | Elecy | Labour | SWR10108 | 629.85 | EA | 2519.4
17 | 8 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | Elecy | Labour | SWR10642 | 512.55 | EA | 4100.4
18 | 2 | Assembly and erection of Structure as per specification which includes fixing of top channels and cross bracings, transport of all materials from road side to the location, earthing, back filling with earth ramming etc excluding pit excavation and concreting. 33 KV DP Structure with 175x85/150x75mm RS joist | Elecy | Labour | SWR11276 | 5670 | SET | 11340
19 | 4 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation Box pole 9/10/11 Mtr | Elecy | Labour | SWR11266 | 2643.83 | EA | 10575.32
20 | 3.9 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. | Elecy | Supply | SMR40009 | 2181 | TO | 8505.9
21 | 3.9 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. | Elecy | Supply | SMR40010 | 1293 | TO | 5042.7
22 | 3.9 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium | Elecy | Labour | SWR10877 | 851 | TO | 3318.9
23 | 3.9 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium | Elecy | Labour | SWR10879 | 482 | TO | 1879.8
24 | 26 | Loading of 11KV/33KV XLPE UG Cable for all sizes | Elecy | Labour | SWR11230 | 1024 | DR | 26624
25 | 26 | Un loading of 11KV/33KV XLPE UG Cable for all sizes | Elecy | Labour | SWR11231 | 1024 | DR | 26624
26 | 13 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Above 30 Km and upto 50 Km with Lorry for each trip | Elecy | Labour | SWR11863 | 4372.74 | EA | 56845.62
27 | 6 | Loading of 33 KV, 10 KA LAs Station type | Elecy | Labour | SWR10266 | 41 | EA | 246
28 | 6 | Un loading of 33 KV, 10 KA LAs Station type | Elecy | Labour | SWR10584 | 35 | EA | 210
29 | 2 | Erection of 33 KV LAS station/Line type including earthing | Elecy | Labour | SWR10396 | 880 | SET | 1760
30 | 50 | Supply of MS bolts & nuts and washers etc of all sizes | Elecy | Supply | SMR11487 | 91.25 | KG | 4562.5
31 | 0.25 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes (0.031Cumt.) | Elecy | Labour | SWR11890 | 3893 | M3 | 973.25
32 | 8.4 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. Including the cost of cement | Elecy | Labour | SWR10356 | 6579 | M3 | 55263.6
33 | 1 | Submission of auto CAD Drawing as per pole schedule (Detailed survey and sketch) Up to 10 km | Elecy | Labour | SWR12104 | 6000 | LS | 6000
34 | 40 | Supply & Erection of Smart RFID marker | Elecy | Supply | SWR25089 | 2745 | EA | 109800
35 | 436 | Supply of 9" B Class GI pipe | Elecy | Supply | SMR40082 | 1113 | M | 485268
36 | 470 | Supply of 250 mm Hume pipe of class NP3 with compresive strength of 35N/mm2 for 28 days curing,barewall thickness of 30mm,1.25kG linear/ meter and withstanding capability of 22.50KN/linear meter as per IS 458-1993. | Elecy | Supply | SMR40077 | 363 | M | 170610
37 | 3700 | Consultation charges for providing traffic diversions and meeting other exegencies for execution of work during late night hours and wee hours. | Elecy | Labour | SWR21903 | 30 | M | 111000
38 | 2 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | Elecy | Labour | SWR12331 | 146.63 | EA | 293.26
39 | 2 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Elecy | Labour | SWR10881 | 142 | EA | 284
40 | 6 | Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication | Elecy | Supply | SMR11482 | 3486 | EA | 20916
41 | 6 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50M height | Elecy | Labour | SWR10359 | 386 | EA | 2316
42 | 6 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elecy | Labour | SWR10357 | 1234.2 | EA | 7405.2
43 | 2765 | Laying of 33KV XLPE UG cable Double Run of Size in Hard Rock (1.2*0.5x1=0.6cum) | Elecy | Labour | SWR11002 | 1430 | RMT | 3953950
Total Amount | [7 empty] | 6939578.652
GST 18% | [7 empty] | 1249124.1574
Schedule Amount | [7 empty] | 8188702.8094