## Stretch I
Name of the work:Shifting of 33KV&11KV Lines, DTRs & Erection of 11KV RMUs at Stretch -I: Shankarpally road to Neo-Polis Circle for Integrated Development of Kokapet Layout including construction of Trumpet and interchange at Narsingi (V)of Ibrahimbagh Division of ECGH Division in Master Plan/Rangareddy Circle under DC Works Estimate Number:Y-2021-13-03-02-01-004
Estimate Quantity | Item Detailed Specification Description | Work Type eg. Earth Work, Electrical works. Etc | Item Short Description | APSS / Morth Cl. Number | Rate (INR) | UOM | Amount
250 | Raising of double run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) - 33 KV 3x400 Sqmm Cable | Elec | Labour | SWR12004 | 323.85 | M | 80962.5
100 | Supply of GI Bolts & Nuts etc | Elec | Supply | SMR11488 | 117.5 | M | 11750
24 | Loading of 11KV/33KV XLPE UG Cable for all sizes | Elec | Labour | SWR11230 | 1024 | M | 24576
24 | Un loading of 11KV/33KV XLPE UG Cable for all sizes | Elec | Labour | SWR11231 | 1024 | M | 24576
12 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)- Above 30 Km and upto 50 Km with Lorry for each trip | Elec | Labour | SWR11863 | 4372.74 | M | 52472.88
75 | Supply of RCC cable Joint markers/ Cable route markers of size 700 X 240 X 75 mm duly engraving with 5 mm thick letters , CPDCL 33000/11000 Cable/Cable joint fixing the 300mm below ground level and 400mm above ground level confirming to IS 5820 2001 | Elec | Supply | SMR40085 | 484 | EA | 36300
150 | Supply of earthing pipe with materials-Supply of GI Flat 25X3 mm | Elec | supply | SMR11485 | 105 | DR | 15750
8 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | Elec | Labour | SWR10642 | 513 | DR | 4104
3.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub- station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.-Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. | Elec | Supply | SMR40009 | 2181 | EA | 8178.75
3.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.-(*)Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc.(*) Note:-The requirement of 2nd coat is to be justified by the concerned Divisional Engineer /Executive Engineer before execution of this work | Elec | Supply | SMR40010 | 1293 | KG | 4848.75
3.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub- station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete- Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium | Elec | Labour | SWR10877 | 851 | EA | 3191.25
3.75 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.-(*) Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium .(*) Note:-The requirement of 2nd coat is to be justified by the concerned Divisional Engineer /Executive Engineer before execution of this work | Elec | Labour | SWR10879 | 482 | KG | 1807.5
10 | Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication | Elec | Supply | SMR11482 | 3486 | EA | 34860
5 | Erection of 33 KV AB Switch including alignment and earthing | Elec | Labour | SWR10392 | 4500 | EA | 22500
4 | Erection of OH Lines including AB Cable (33KV, 11KV, LT)-Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation- Box pole 9/10/11 Mtr | Elec | Labour | SWR11266 | 2643.83 | EA | 10575.32
5 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation-Erection of 5 Mts RS Joist (Bit) Pole including fixing of Pole Mounted Box | Elec | Labour | SWR20863 | 1044.23 | M3 | 5221.15
3 | Excavation of pits in all soils except hard rock requiring blasting-11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M (1.31 cum) | Elec | Labour | SWR10108 | 630 | M3 | 1890
6 | Excavation of pits in hard rock requiring blasting. (other than SS)-11Mtrs PSCC Pole/ Box poles 0.75 M x 0.9 M x 1.95 M | Elec | Labour | SWR10113 | 1326 | M | 7956
11.7 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc.- Including the cost of cement | Elec | Supply | SWR10356 | 6579 | EA | 76974.3
2000 | Supply of 9" B class GI pipe | Elec | Supply | SMR40082 | 1113 | SET | 2226000
32 | UG cable-Making of Straight through joints-33 KV 3x400 Sqmm Cable | Elec | Labour | SWR10382 | 5700.78 | TO | 182424.96
28 | Making of Outdoor/Indoor End Termination - 33 KV 3x400 Sqmm Cable | Elec | Labour | SWR10387 | 2764.76 | TO | 77413.28
0.15 | Paving out and stringing of conductor by providing temporary stays, tensioning, sagging correctly, fixing strain points, transferring to pin points binding, keeping stifner, rectification of poles, guys and jumpering etc., including transport of material from road side to location.-100 Sqmm Single Circuit (3 Conductors) | Elec | Labour | SWR10366 | 13856.73 | TO | 2078.51
2 | Formation of Cut point for 33 KV Single Circuit line excluding pole erection and stays | Elec | Labour | SWR10981 | 1791.12 | TO | 3582.24
0.15 | survey line&cabl inc peg mark&tree clear | Elec | Labour | SWR22092 | 765 | TO | 114.75
14.256 | Earth work excavation of pits in hard murram/rock boulders | Elec | Labour | SWR20959 | 1530 | M3 | 21811.68
3 | Supply of M+3 Tower (Galvanized) | Elec | Supply | SMR11683 | 140674.3 | M | 422022.9
3 | Erection of M+3 Tower (Galvanized) | Elec | Labour | SWR11850 | 64576 | TO | 193728
6 | Supply of material for Extension of 3Mtrs for M+3 (Galvanized) | Elec | Supply | SMR11684 | 28520.64 | TO | 171123.84
6 | Erection of Extension of 3Mtrs for M+3 (Galvanized) | Elec | Labour | SWR11851 | 5168.95 | TO | 31013.7
2 | Erection of 33 KV LAS station/Line type including earthing | Elec | Labour | SWR10396 | 880 | TO | 1760
1800 | Hard Rock Cutting 11KV- Consultation charges for providing traffic diversions and meeting other exegencies for execution of work during late night hours and wee hours. | Elec | Labour | SWR21903 | 30 | TO | 54000
15.48 | Loading of MS Scrap | Elec | Labour | SWR10258 | 578 | EA | 8947.44
1.68 | Loading of ACSR conductor scrap | Elec | Labour | SWR10257 | 491 | EA | 824.88
1.68 | Un loading of ACSR conductor scrap | Elec | Labour | SWR10575 | 491 | EA | 824.88
15.48 | Un loading of MS Scrap | Elec | Labour | SWR10576 | 578 | EA | 8947.44
18.83 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading )-Above 30 KM and upto 50 KM | Elec | Labour | SWR10134 | 587.52 | EA | 11063
2 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading)- Above 30 Km and upto 50 Km with Lorry for each trip | Elec | Labour | SWR11863 | 4372.74 | EA | 8745.48
16 | S&E-Smart RFID marker | Elec | Supply & Labour | SWR25089 | 2745 | TO | 43920
10 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elec | Labour | SWR10357 | 1234.2 | TO | 12342
10 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height | Elec | Labour | SWR10359 | 386 | TO | 3860
4000 | Laying of Second 33KV UG Cb in Existing Duct | Elec | Labour | SWR12452 | 200 | TO | 800000
250 | Laying of 33KV XLPE UG cable Double Run of Size in Hard Rock(1.2*0.5x1=0.6cum) | Elec | Labour | SWR11002 | 1430 | TO | 357500
250 | Excavation & laying of UG Cable (Four Run )-Laying of XLPE UG cable Four Run including excavation of trench of size 1050mm wide to 1200mm wide as per the site conditions and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second,third or more cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs.-Along the CC / BT multi layer road requiring compressor-33 KV 3x400 Sqmm Cable | Elec | Labour | SWR12040 | 2103.75 | EA | 525937.5
1 | Erection of 33KV 3 Way RMU | Elec | Labour | SWR11335 | 5775 | KM | 5775
1 | Raising of RMU plinth with Bricks 4 sides including crane cost, labour with white washing excluding cable jointing for 3 Way/5 Way RMUs | Elec | Labour & Supply | SWR12210 | 4200 | EA | 4200
2000 | Laying of 2nd cable in excavated trench | Elec | Labour | SWR10988 | 204.1 | EA | 408200
250 | Excavation & laying of UG Cable (Four Run )-Laying of XLPE UG cable Four Run including excavation of trench of size 1050mm wide to 1200mm wide as per the site conditions and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second,third or more cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs.-Across the CC/ BT road crossing multi layer road requiring compressor (excluding the cost of Hume pipe)-33 KV 3x400 Sqmm Cable | Elec | Labour | SWR12045 | 2244 | EA | 561000
1.8 | Dismantling of 100 sqmm Conductor DC | Elec | Labour | SWR22064 | 11816.7 | EA | 21270.06
0.3 | Dismantling of 100 Sqmm AAA/ACSR Conductor | Elec | Labour | SWR22063 | 8274.77 | M | 2482.43
10 | Dismatling of M type tower | Elec | Labour | SWR11122 | 3484 | DR | 34840
10 | Dimantle-Extension of M+3 Tower | Elec | Labour | SWR12480 | 2584.48 | DR | 25844.8
22 | Dism of Rail pole 90 lbs | Elec | Labour | SWR11322 | 900 | EA | 19800
200 | Excavation & laying of UG Cable in Single Run-Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs.-In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil / CC/BT Road-11 KV 3x300 Sqmm Cable | Elec | Labour | SWR11919 | 465 | EA | 93000
800 | Excavation & laying of UG Cable in Single Run-Laying of XLPE UG cable including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs.-Along the CC / BT multi layer road requiring compressor-11 KV 3x300 Sqmm Cable | Elec | Labour | SWR11928 | 1074 | KG | 859200
1700 | Laying of11KV XLPE UG cable Double Run of Size in Hard Rock(1.05*0.5x1=0.525cum) | Elec | Labour | SWR11004 | 1194 | EA | 2029800
1000 | Supply of 6" B class GI pipe | Elec | Supply | SMR40081 | 1044 | M3 | 1044000
2450 | Laying of XLPE UG cable Six Run including excavation of trench of size 1050mm wide to 1200mm wide as per the site conditions and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second,third or more cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs.Across the CC/ BT road crossing multi layer road requiring compressor (excluding the cost of Hume pipe)-Laying of 2nd cable in excavated trench | Elec | Labour | SWR10988 | 204.1 | M3 | 500045
20 | Making of Outdoor/Indoor End Termination- 11 KV 3x300 Sqmm Cable | Elec | Labour | SWR10391 | 2370.63 | EA | 47412.6
20 | UG cable-Making of Straight through joints-11 KV 3x300 Sqmm Cable | Elec | Labour | SWR10386 | 3725.45 | EA | 74509
13 | Loading of 11KV/33KV XLPE UG Cable for all sizes | Elec | Labour | SWR11230 | 1024 | EA | 13312
13 | Un loading of 11KV/33KV XLPE UG Cable for all sizes | Elec | Labour | SWR11231 | 1024 | EA | 13312
6 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) - Above 30 Km and upto 50 Km with Lorry for each trip | Elec | Labour | SWR11863 | 4372.74 | EA | 26236.44
2 | Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | Elec | Labour | SWR10393 | 3200 | KG | 6400
2 | Erection of OH Lines including AB Cable (33KV, 11KV, LT)-Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation- Box pole 9/10/11 Mtr | Elec | Labour | SWR11266 | 2643.83 | M | 5287.66
2.1 | Earth work excavation of pits in hard murram/rock boulders | Elec | Labour | SWR20959 | 1530 | EA | 3213
2.1 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc.- Including the cost of cement | Elec | Supply & Labour | SWR10356 | 6579 | EA | 13815.9
3 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) Note: 1). It will be treated as full load of 10 MT and paid for 10 MT. 2). For 3 Ton vehicle : 50% of the following rates-Above 30 Km and upto 50 Km with Lorry for each trip | Elec | Labour | SWR11863 | 4372.74 | EA | 13118.22
5 | Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication | Elec | Labour | SMR11482 | 3486 | EA | 17430
0.1 | Paving out and stringing of conductor by providing temporary stays, tensioning, sagging correctly, fixing strain points, transferring to pin points binding, keeping stifner, rectification of poles, guys and jumpering etc., including transport of material from road side to location.-55 Sqmm Single Circuit (3 Conductors) | Elec | Labour | SWR10365 | 9454.8 | EA | 945.48
8 | Formation of Cut point for 11 KV Single Circuit line excluding pole erection and stays | Elec | Labour | SWR10653 | 1435.81 | EA | 11486.48
100 | Supply of GI Flat 25X3 mm | Elec | Labour | SMR11485 | 105 | EA | 10500
100 | Supply of RCC cable Joint markers/ Cable route markers of size 700 X 240 X 75 mm duly engraving with 5 mm thick letters , CPDCL 33000/11000 Cable/Cable joint fixing the 300mm below ground level and 400mm above ground level confirming to IS 5820 2001 | Elec | Supply & Labour | SMR40085 | 484 | EA | 48400
4 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5 meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | Elec | Labour & Supply | SWR10642 | 513 | KG | 2052
1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.-Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. | Elec | Supply | SMR40009 | 2181 | EA | 2181
1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.-(*)Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc.(*) Note:-The requirement of 2nd coat is to be justified by the concerned Divisional Engineer /Executive Engineer before execution of this work | Elec | Supply | SMR40010 | 1293 | M3 | 1293
1 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.-Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium | Elec | Labour | SWR10877 | 851 | M3 | 851
1 | (*) Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium .(*) Note:-The requirement of 2nd coat is to be justified by the concerned Divisional Engineer /Executive Engineer before execution of this work | Elec | Labour | SWR10879 | 482 | RMT | 482
240 | Consultation charges for providing traffic diversions and meeting other exegencies for execution of work during late night hours and wee hours. | Elec | Labour | SWR21903 | 30 | M | 7200
13 | S&E-Smart RFID marker | Elec | Supply & Labour | SWR25089 | 2745 | M | 35685
21 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elec | Labour & Supply | SWR10357 | 1234.2 | M | 25918.2
21 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50 M height | Elec | Supply & Labour | SWR10359 | 386 | M | 8106
28.764 | Fabrication of Main and Auxiliary structures with welding using raw steel such as RS joist, M.S.Angles, Plates, Channels, including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Elec | Supply & Labour | SWR10869 | 3426 | TO | 98545.46
28.764 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.-Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. | Elec | Supply | SMR40009 | 2181 | TO | 62734.28
28.764 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.-(*)Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc.(*) Note:-The requirement of 2nd coat is to be justified by the concerned Divisional Engineer /Executive Engineer before execution of this work | Elec | Supply | SMR40010 | 1293 | TO | 37191.85
28.764 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.-Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium | Elec | Labour | SWR10877 | 851 | TO | 24478.16
28.764 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete.-(*) Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium .(*) Note:-The requirement of 2nd coat is to be justified by the concerned Divisional Engineer /Executive Engineer before execution of this work | Elec | Labour | SWR10879 | 482 | TO | 13864.25
5 | Erection of 11KV 3 Way RMU | Elec | Labour | SWR10664 | 2051.48 | KM | 10257.4
5 | Loading of 11KV 3 Way RMU/Twin feeder panel | Elec | Labour | SWR10615 | 907.8 | EA | 4539
5 | Raising of RMU plinth with Bricks 4 sides including crane cost, labour with white washing excluding cable jointing for 3 Way/5 Way RMUs | Elec | Labour & Supply | SWR12210 | 4200 | EA | 21000
15 | Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication | Elec | Supply | SMR11482 | 3486 | EA | 52290
50 | Raising of double run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe)-33 KV 3x400 Sqmm Cable | Elec | Labour | SWR12004 | 323.85 | EA | 16192.5
2 | Dismantling of 11KV 34/55 sqmm SC | Elec | Labour | SWR22065 | 4500 | EA | 9000
10 | Dism of 9.1M PSCC Pole | Elec | Labour | SWR11320 | 948.09 | EA | 9480.9
0.3 | Dismantling of 11KV 34/55 sqmm SC | Elec | Labour | SWR22065 | 4500 | SET | 1350
Total Estimate | [6 empty] | 11958008.95
Service Tax 18% Rs. | [6 empty] | 2152441.611
Grand Total Rs. | [6 empty] | 14110450.561